REGULATORY REQUIREMENTS TO BE FULLFILLED BY RENEWABLE ENERGY GENERATORS BEFORE COMMISSIONING OF THE PROJECT AND GETTING CONNECTED WITH MP GRID

1. Registration Fee: Registration Fee of ` 5000/- for registration with SLDC is to be deposited in the SLDC account, details may be obtained from SLDC. The Registration form (Annexure-A) should be submitted to SLDC.

2.  TELEMETRY & COMMUNICATION : The Data Acquisition facility (Telemetry) for transfer of pooling station wise and turbine wise / inverter wise telemetry data along  with whether parameters to SLDC/Sub LDCs should be established alongwith communication facility in accordance with the guidelines specified in Annexure – B.

3. ABT Metering with AMR: ABT meters of 0.2s accuracy class and of open protocol conforming to IS: 15959 with AMR facility. This is to be provided at the pooling sub-station / Interface point for the purpose of energy accounting. Also provide the ABT meter and metering equipments details dully certified by MPPTCL / Discoms in the format as Annexure-I. The ABT meters should have AMR facility for providing meter data to SLDC.

To do this you have to install modem and SIM (capable of working on both GPRS & GSM network) enabled at the interface point and integrating the meters with the AMR system of Secure make installed at SLDC which has the static IP address 117.239.195.194, for data transfer between energy meter and AMR system at SLDC over the GSM/GPRS communications network. The integration of ABT meters with AMR system could be done with the help of M/s Secure or any other competent vendor.

After integration of ABT meters with AMR system, you have to obtain a confirmation from SLDC that the meters are integrated with AMR system and data of ABT meters are being successfully downloaded through AMR system.

4.  Single line diagram indicating the connectivity with the grid duly certified by:

(i)  MPPTCL when connected to 132 KV and above

(ii) DISCOM when connected at 33 KV and below at MPPTCL / DISCOM substation.

5.  Copy of connection agreement with MPPTCL or DISCOM as the case may be.

6.  Information regarding sale of power to MPPMCL / Third party sale (Copy of PPA & LTA). In case of Third Party sale / Captive Use, the Wheeling Agreement / Consent letter from MPPMCL / Discoms is required.

7.  Copy of approval from Chief Electrical Inspector.

8.  Information required for Renewable Energy Management Centre (REMC) in REMC format.

9.  In accordance with CEA (Technical Standards for connectivity)-Regulations-2013(Part-II) and directions issued by Hon’able CERC in their order dated 05.01.2016, the Wind Electric Generators (WTGs) of capacity equal to or more than 500KW except “Stall Type WTGs” and Solar Generators whose bidding process was not commenced on 05.01.2016 and connected at voltage level 132KV and above should have “Low Voltage Ride Through (LVRT) Capability” in their Generating Stations and are required to furnish the information as per LVRT format.

10.  The Central Electricity Authority (Technical Standards for Construction of Electrical Plants and Electrical Lines), Section 88(5) mandates that “The owner shall arrange all required consents and approvals including as those from Power Telecommunication Coordination Committee (PTCC); and for civil aviation, road, river, rail, canal or power line crossing, way leaves and environment & forest clearances etc. from the concerned Authorities, agencies. In order to comply the above requirement, the transmission licensee / owner may ensure that “PTCC Route Approval” is accorded by the competent authority and submit undertaking for the same as per PTCC Route Approval format.

11. FORECASTING, SCHEDULING AND DEVIATION SETTLEMENT (to commence after commissioning): Hon’able State Commission has notified the MPERC (Forecasting, Scheduling, Deviation Settlement Mechanism and related matters of Wind and Solar Generating Stations) Regulations 2018 on 20th April 2018. These regulations have come into force from the date of notification of regulations. The regulations are applicable to all Wind Generators having a combined installed capacity of 10MW and above and Solar Generators with an installed capacity of 5 MW and above including those connected via pooling statins and selling power within or outside the State. In compliance to the regulatory provisions, all the qualified Wind and Solar Generators shall have to appoint Qualified Coordinating Agency (QCA) which may be one of the Generator or any other mutually agreed agency for the purpose of forecasting / scheduling, metering, data collection/ transmission, communication, Settlement of Deviation Charges, De-pooling of payment and settlement with Generators. The QCA shall be treated as a State Entity and shall have to get registered with SLDC by submitting the dully filled up QCA-Registration Form available at website along with Registration Fee of ` 5000/- in SLDC account. All the qualified wind & solar power projects shall have to submit day ahead Available Capacity (AvC) and load forecasting and real time revisions of their project at pooling sub-station on 15-minute time block as per Forecasting Format in Annexure-III to SLDC at email id – remcjbp@gmail.com and remcjbp@yahoo.com by 10.00hrs daily. The other RE Generators shall also be subjected to scheduling as per 7th Amendment to MPERC (Co-generation and Generation of Electricity from Renewable Sources of Energy) (Revision-I) Regulations, 2010 and shall submit their load forecasting and real time revisions of their project at pooling sub-station on 15 minute time block as per Forecasting Format in Annexure-III to SLDC at email id – remcjbp@gmail.com and remcjbp@yahoo.com by 10.00hrs daily.

12.   The RE Generators are required to provide contact details of Control room /Monitoring centers.

13. RE Generators may also refer updated provisions of the applicable regulations / codes as amended from time to time by the Commission.

# ****